## Wind Load Calculator
Pitched Roof Wind Loading Calculator
PROJECT
Project number
Project Name
Client | [9 empty] | <22 | 22-24 | 24-26 | 26-28 | >28
[10 empty] | <2 | 2-20 | >20
[10 empty] | 5 | 10 | 15 | 20 | 25
INPUTS | [9 empty] | Urban | Country
Site | [9 empty] | Yes | No
Basic wind speed (from map) | >28 | m/s | [7 empty] | Central | Edge | Corner
Site altitude above sea level | 200 | m
Distance from the sea | <2 | km
Location type | Country
Note: | [9 empty] | 5 | 15 | 30 | 45 | 60 | 75
'Country' includes sites less than 0.3km inside town boundary
Installation | [9 empty] | Roof Pitch |  |  | 4
Ridge height | 15 | m
Roof pitch angle | 45 | degrees | [7 empty] | In-roof | On-roof
Panel Type | In-roof
SELECT ROOF ZONE |  |  |  | RESULTS
|  |  |  | Peak velocity pressure (qp) |  | 2572.8 | Pa
|  |  |  | Wind load negative pressure |  | -2830.08 | Pa
|  |  |  | Wind load positive pressure |  | 2058.24 | Pa
|  |  |  | Load partial safety factor |  | 1.35
|  |  |  | Design load | ( - ) | -3821 | Pa
[5 empty] | ( + ) | 2779 | Pa
Cp
Solar Panel Design Resistance
|  | Cp | -1.2 | (Including partial safety factor)
[5 empty] | ( - ) | ( + )
[5 empty] | -5320 | 5400 |  | OK
Clearline fusion design resistance was tested on a representative roof structure and includes material partial safety factors. Tested batten size - 50mm x 25mm, rafter 35mm x 75mm, rafter spacing 600mm For sarking brackets - softwood sarking boards 100mm x 22mm. Wind resistance according to MCS012, positive design load to IEC61215
Worst Case Negative Pressure Coefficient |  | Cp | -1.1
Worst Case Positive Pressure Coefficient |  | Cp | 0.8
(According to Eurocode 1, EN 1991-1-4 )
The calculation is based on the simplified wind loading method given in Annex B of the MCS PV Guide. Topography is assumed to be insignificant, marked edge zones of pitched roofs are assumed avoided. Viridian Solar offers no warranty as to the accuracy of this tool. If in doubt, consult a structural engineer.
For use with Viridian Solar Clearline fusion solar panels only
www.viridiansolar.com | [8 empty] | © Viridian Solar 2019
Version 1.4

## Calculation (hidden)
Wind Loading Pressure for Solar Panel on Pitched Roof | [8 empty] | qp (Pa)
[12 empty] | Country |  |  | Urban
[9 empty] | Wind Speed | Ridge Height | <2 | 2-20 | >20 | <2 | 2-20 | >20
Lookup Qp | [8 empty] | <22 | 5 | 869 | 783 | 718 | 688 | 620 | 569
[9 empty] | <22 | 10 | 1009 | 955 | 872 | 883 | 836 | 763
Offset ridge | 3 | [7 empty] | <22 | 15 | 1094 | 1062 | 977 | 1012 | 982 | 904
Offset distance | 1 | [7 empty] | <22 | 20 | 1122 | 1108 | 1017 | 1066 | 1052 | 966
[9 empty] | <22 | 25 | 1166 | 1166 | 1072 | 1137 | 1137 | 1045
| Country | Urban
<22 | 1094 | 1012 | [6 empty] | 22-24 | 5 | 1034 | 931 | 854 | 819 | 738 | 677
22-24 | 1302 | 1204 | [6 empty] | 22-24 | 10 | 1201 | 1136 | 1038 | 1050 | 994 | 908
24-26 | 1527 | 1413 | [6 empty] | 22-24 | 15 | 1302 | 1264 | 1163 | 1204 | 1169 | 1075
26-28 | 1772 | 1639 | [6 empty] | 22-24 | 20 | 1335 | 1318 | 1210 | 1268 | 1253 | 1149
>28 | 2144 | 1983 | [6 empty] | 22-24 | 25 | 1388 | 1388 | 1276 | 1353 | 1353 | 1244
Offset Zone | 5 | [7 empty] | 24-26 | 5 | 1213 | 1093 | 1003 | 961 | 866 | 794
Offset Location | 1 | [7 empty] | 24-26 | 10 | 1409 | 1334 | 1218 | 1233 | 1167 | 1066
[9 empty] | 24-26 | 15 | 1527 | 1483 | 1364 | 1413 | 1372 | 1262
[9 empty] | 24-26 | 20 | 1567 | 1547 | 1420 | 1489 | 1470 | 1349
[9 empty] | 24-26 | 25 | 1629 | 1629 | 1498 | 1588 | 1588 | 1460
Lookup qp 100m altitude | 2144
[9 empty] | 26-28 | 5 | 1407 | 1268 | 1163 | 1115 | 1004 | 921
Correction factor altitude >100 | 1.2 | [7 empty] | 26-28 | 10 | 1634 | 1547 | 1413 | 1430 | 1353 | 1236
[9 empty] | 26-28 | 15 | 1772 | 1720 | 1582 | 1639 | 1591 | 1464
[9 empty] | 26-28 | 20 | 1817 | 1795 | 1647 | 1726 | 1705 | 1565
qp | 2572.8 | [7 empty] | 26-28 | 25 | 1889 | 1889 | 1737 | 1842 | 1842 | 1694
[9 empty] | >28 | 5 | 1703 | 1534 | 1407 | 1349 | 1215 | 1115
Cp max negative | -1.1 | [7 empty] | >28 | 10 | 1977 | 1872 | 1710 | 1730 | 1638 | 1496
Cp max positive | 0.8 | 45 | 4 | [5 empty] | >28 | 15 | 2144 | 2081 | 1915 | 1983 | 1925 | 1771
[9 empty] | >28 | 20 | 2199 | 2171 | 1993 | 2089 | 2063 | 1893
[9 empty] | >28 | 25 | 2286 | 2286 | 2102 | 2229 | 2229 | 2049
External Pressure
Pe = qp Cp
Ca = 1 for an element as small as a solar panel
Cp,net from lookup table
Worst Case NEGATIVE Pressure coefficients from EUROCODE 1: | [11 empty] | Worst Case POSITIVE Pressure coefficients from EUROCODE 1:
Table NA6a External pressure coefficients for monopitch roofs | [11 empty] | Table NA6a External pressure coefficients for monopitch roofs
|  | Ɵ = 0 ,180 |  |  | Ɵ = 90 | [8 empty] | Ɵ = 0 ,180 |  |  | Ɵ = 90
Pitch Angle | F | G | H | G | H | I | [5 empty] | Pitch Angle | F | G | H | G | H | I
5 | -2.4 | -1.2 | -0.8 | -1.1 | -0.7 | -0.7 | [5 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 0
15 | -2.6 | -1 | -0.9 | -1.1 | -0.8 | -0.8 | [5 empty] | 15 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
30 | -1.7 | -1 | -0.9 | -1.2 | -1 | -0.8 | [5 empty] | 30 | 0.8 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2
45 | -0.9 | -0.8 | -0.9 | -1.2 | -1 | -0.9 | [5 empty] | 45 | 0.8 | 0.6 | 0.7 | 0.5 | 0.4 | 0.3
60 | -1 | -0.7 | -0.7 | -1.2 | -0.4 | -0.2 | [5 empty] | 60 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5
75 | -1.1 | -0.7 | -0.7 | -1.2 | -0.4 | -0.2 | [5 empty] | 75 | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.6
Table 10 External pressure coefficients Cpe for duopitch roofs | [11 empty] | Table 10 External pressure coefficients Cpe for duopitch roofs
| Ɵ = 0 |  | Ɵ = 90 | [9 empty] | Ɵ = 0 |  | Ɵ = 90
Pitch Angle | H | I | H | I | [7 empty] | Pitch Angle | H | I | H | I
5 | -0.6 | -0.4 | -0.6 | -0.5 | [7 empty] | 5 | 0 | 0 | 0 | 0
15 | -0.4 | -0.5 | -0.6 | -0.4 | [7 empty] | 15 | 0.2 | 0 | 0.2 | 0.2
30 | -0.2 | -0.5 | -0.6 | -0.5 | [7 empty] | 30 | 0.4 | 0 | 0.3 | 0.2
45 | 0 | -0.5 | -0.6 | -0.4 | [7 empty] | 45 | 0.7 | 0 | 0.4 | 0.3
60 | 0 | -0.6 | -0.7 | -0.6 | [7 empty] | 60 | 0.8 | 0 | 0.5 | 0.5
75 | 0 | -0.8 | -0.7 | -0.6 | [7 empty] | 75 | 0.8 | 0 | 0.7 | 0.6
Table 10 External pressure coefficients Cpe for hipped roofs | [11 empty] | Table 10 External pressure coefficients Cpe for hipped roofs
Pitch Angle | F | G | H | I | J | K | L | M | N |  |  | Pitch Angle | F | G | H | I | J | K | L | M | N
5 | -1.8 | -1.2 | -0.6 | -0.6 | -0.8 | -0.6 | -1.1 | -0.6 | -0.6 |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | -1.3 | -0.8 | -0.5 | -0.6 | -1.4 | -1.3 | -0.9 | -0.6 | -0.4 |  |  | 15 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0
30 | -0.5 | -0.5 | -0.2 | -0.6 | -1.3 | -0.8 | -1 | -0.6 | -0.5 |  |  | 30 | 0.8 | 0.5 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
45 | 0 | 0 | 0 | -0.6 | -0.7 | -0.4 | -1.1 | -0.6 | -0.4 |  |  | 45 | 0.8 | 0.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0 | 0 | 0 | -0.7 | -0.6 | -0.3 | -1.2 | -0.7 | -0.6 |  |  | 60 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
75 | 0 | 0 | 0 | -1.2 | -0.6 | -0.3 | -1.2 | -0.7 | -0.6 |  |  | 75 | 0.8 | 0.8 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
Worst Case negative pressure coefficient for each roof type | [11 empty] | Worst Case positive pressure coefficient for each roof type | bar: F to I
Pitch Angle | F: 1; G: 2; H: 3; I: 4 |  |  | Pitch Angle | 1 | 2 | 3 | 4
5 | F: -0.8; G: -0.6; H: -0.6; I: -1.8 |  |  | 5 | 0 | 0 | 0 | 0
15 | F: -0.9; G: -0.6; H: -0.6; I: -1.4 |  |  | 15 | 0.2 | 0.2 | 0.2 | 0.2
30 | F: -1; G: -0.6; H: -0.6; I: -1.3 |  |  | 30 | 0.4 | 0.4 | 0.4 | 0.8
45 | F: -1; G: -0.6; H: -0.6; I: -1.1 |  |  | 45 | 0.7 | 0.7 | 0.7 | 0.8
60 | F: -0.7; G: -0.7; H: -0.7; I: -1.2 |  |  | 60 | 0.8 | 0.8 | 0.8 | 0.8
75 | F: -0.7; G: -0.8; H: -1.2; I: -1.2 |  |  | 75 | 0.8 | 0.8 | 0.8 | 0.8